## Comments
PROJECT: Auto Extracted
TITLE: PDF Comments
Page | Author | Comment
2 | Red Text | Secondary Side of
2 | Red Text | Instrument Signals shall be
2 | Red Text | on Right Side of ETS PLC
2 | Red Text | Primary Side of Instrument
2 | Red Text | Signals shall be on Left Side
2 | Red Text | of ETS PLC
2 | Red Text | IC-PS-FCV-A
2 | Red Text | PC-PS-FCV-A
2 | Red Text | Add following Abbreviations
2 | Red Text | IC : Instrument Cable
2 | Red Text | PC : Power Cable
2 | Red Text | SHLD. : Shield
2 | Red Text | PLC
2 | Red Text | Increase Font Size to
2 | Red Text | match other Text.
2 | Red Text | OEM supplied Cables
2 | Red Text | INSTRUMENT CABLE
2 | Red Text | POWER CABLE
2 | Red Text | CHANGE ALL
2 | Red Text | CABLE TAGS
2 | Red Text | IN SIMILAR
2 | Red Text | WAY.
2 | Red Text | MAKE TAG NUMBERING
2 | Red Text | PHILOSOPHY HERE.
2 | Red Text | Show MODBUS Cable
2 | Red Text | instead of HW for VFD's.
2 | Red Text | Show PLC Panel 230VAC
2 | Red Text | Power Incomer.
2 | Red Text | Flowmeter Power Cable is Not
2 | Red Text | from BTU. Check and correct.
2 | Red Text | i). Show 2 nos. of FO Patch
2 | Red Text | Cords to FOPP
2 | Red Text | ii). Show 2 nos. of 24C FOC
2 | Red Text | towards Main Plant FO
2 | Red Text | Network (as per Architecture)
2 | lenovo | Secondary Side of Instrument Signals shall be on Right Side of ETS PLC
2 | lenovo | Primary Side of Instrument Signals shall be on Left Side of ETS PLC
2 | lenovo | IC-PS-FCV-A
2 | lenovo | PC-PS-FCV-A
2 | lenovo | Add following Abbreviations IC : Instrument Cable PC : Power Cable SHLD. : Shield PLC
2 | lenovo | Increase Font Size to match other Text.
2 | lenovo | OEM supplied Cables
2 | lenovo | INSTRUMENT CABLE
2 | lenovo | POWER CABLE
2 | lenovo | CHANGE ALL CABLE TAGS IN SIMILAR WAY.
2 | lenovo | MAKE TAG NUMBERING PHILOSOPHY HERE.
2 | lenovo | Show MODBUS Cable instead of HW for VFD's.
2 | lenovo | Show PLC Panel 230VAC Power Incomer.
2 | lenovo | Flowmeter Power Cable is Not from BTU. Check and correct.
2 | lenovo | i). Show 2 nos. of FO Patch Cords to FOPP ii). Show 2 nos. of 24C FOC towards Main Plant FO Network (as per Architecture)